|  | ......... pcs. .................. € .................. € GEZE MBZ 300 N8 Modular bus control panel for smoke and heat extraction and ventilation. For controlling 24 V DC electric drives with an overall power consumption of 8 ampere. Commissioning with default settings without further parameter setting makes fast and straightforward installation possible. USB interface for the comprehensive parameter setting using MBZ 300 PC configuration software. The control panel has free slots for a further module and can be extended by: - vent group (Drive Module DM) - status contacts (relay module ERM) - weather sensors (weather module WM) Automatic battery charger for temperature-compensated charging with monitoring of the charging equipment Automatic switchover from mains to battery operation Emergency power supply with rechargeable battery 2 x 12 V for at least 72 hours Possible connections: - Rain/wind control - Smoke detector and/or heat detector - FT 4 SHEV button - Vent switch with or without LED function display - Alarm input for external release (fire alarm system) Technical data: Input voltage: 230 V AC Output voltage: 24 V DC Residual ripple: 2 % Integrated service interval display IP rating: IP54 Output current max. 8 A Tested in accordance with EN12010-10 and VdS approved Steel cabinet with two-way key bit lock, painted grey (RAL 7035) Width: 300 mm Height: 400 mm Depth: 200 mm One alarm group with: Connection of automatic detectors and line monitoring in - max. two separately evaluated lines - max. 10 each Connection option for a line-monitored external potential-free contact e.g. fire alarm system Connection of SHEV buttons with line monitoring Inputs for central vent switch Parameters for push button properties can be set for - Dead man or latching - Automatic step - Automatic ventilation Potential-free status contact for alarm or fault, parameters can be set Status display for the module and connected components via LEDs for high operating comfort during installation and servicing. One vent group with: 8 A switching current Status inputs for which parameters can be set - as inhibiting input for sequence control with shades - as input for feedback of the end positions OPEN and CLOSED Parameters for push button properties can be set for - Dead man or latching - Automatic step - Automatic ventilation Motor connection with line monitoring Supply to holding magnets possible Activation of pressure gas generators Short-circuit proof due to automotive flat fuse Direct activation of the module via operating buttons on the module for convenient start-up Status display for the module and connected components via LEDs for high operating comfort during installation and servicing. |
| --- | --- |
|  | ......... pcs. .................. € .................. € GEZE MBZ 300 DM drive module For use in the GEZE MBZ 300 modular bus emergency power control panel For controlling 24 V DC electric drives with max. 8 ampere switching current. |
|  | ......... pcs. .................. € .................. € GEZE MBZ 300 series terminal set For use in the GEZE MBZ 300 modular bus emergency power control panel For the connection of drives with larger cable diameter e.g. to the DME |
|  | ......... pcs. .................. € .................. € GEZE MBZ 300 SM sensor module For use in the GEZE MBZ 300 modular bus emergency power control panel For evaluating line-monitored alarm lines, formation of fire sections and ventilation control |
|  | ......... pcs. .................. € .................. € GEZE MBZ 300 WM weather module For use in the GEZE MBZ 300 emergency power control panel For the evaluation of weather sensors and / or for the activation of smoke and heat extraction windows (SHEV) depending on the wind direction. Lockable components for different requirements: GEZE rain/wind control with potential-free contacts for ventilation GC 401 RS rain sensor and GC 402 WVS wind sensor with adjustment of the max. wind speed for ventilation via the MBZ 300 software GC 401 RS rain sensor and GC 402 WVS wind sensor and GC 403 WDS wind direction sensor as complete activation for SHEVs depending on the wind direction in accordance with EN 12101 Part 2 The settings are made using the MBZ 300 software. Status display for the module and connected components via LEDs for high operating comfort during installation and servicing. |
|  | ......... pcs. .................. € .................. € GEZE MBZ 300 ERM relay module For use in the GEZE MBZ 300 emergency power control panel 6 potential-free status contacts for which parameters can be set for forwarding alarm, fault or ventilation signals The settings are made using the MBZ 300 software. Status display for the module and connected components via LEDs for high operating comfort during installation and servicing. |
|  | ......... pcs. .................. € .................. € GEZE MBZ 300 CAN module For connecting several MBZ 300 panels One CAN module per control panel to be connected is needed. Setting is done using the MBZ 300 software. |
|  | ......... pcs. .................. € .................. € GEZE IO 420 interface module Module for connecting MBZ 300 via input and output terminals or CAN Bus to BACnet MS/TP. Makes activation of the vent groups via GEZE Cockpit possible. Makes visualisation of MBZ 300 alarm and fault messages possible on GEZE Cockpit. |
|  | ......... pcs. .................. € .................. € GEZE FT 4 K/24 V DC SHEV button for manual alarm triggering with alarm and reset button and LED display for "Fire alarm", "Operation", "Window open" and "Fault", in lockable surface-mounted housing marked "Smoke extraction", with break glass pane, plastic housing in the colour: orange similar to RAL 2011 |
|  | ......... pcs. .................. € .................. € GEZE FT4 A/24 V DC SHEV button – VdS for manual alarm triggering with alarm and reset button and LED display for "Fire alarm", "Operation", "Window open" and "Fault", in lockable surface-mounted housing marked "Smoke vent", with break glass pane, die-cast housing in the colour Colour: orange RAL 2011 (VdS approval) Alternatively: ( ) red RAL 3000 ( ) blue RAL 5015 ( ) yellow RAL 1021 ( ) grey RAL 7035 ( ) secondary unit, orange RAL 2011 (only with LED alarm) ( ) acoustic, orange RAL 2011 (with signal in the case of alarm, fault) |
|  | ......... pcs. .................. € .................. € GEZE RM 1003/24 V DC smoke detector with base, for automatic alarm triggering in the case of smoke, VdS-approved version (G 205091) |
|  | ......... pcs. .................. € .................. € GEZE WM 1005/24 V DC heat detector with base for automatic alarm triggering in the case of heat development, VdS-approved version (G 205092) |
|  | ......... pcs. .................. € .................. € GEZE GC 162 RWA smoke detector with base Ceiling-mounted detector for automatically triggering an alarm in the case of smoke, simple testing using an integrated magnetic sensor, Tested in accordance with EN 54-7 |
|  | ......... pcs. .................. € .................. € GEZE GC 163 RWA heat detector with base Ceiling-mounted detector for automatically triggering an alarm in the case of heat build-up, simple testing using an integrated magnetic sensor, Tested in accordance with EN 54-5 |
|  | ......... pcs. .................. € .................. € GEZE vent switch for ventilation mode ( ) AS 500 vent switch LTA-24-AZ with control keys “Open-Close” and LED function display, IP rating IP40, to match switch ranges with 55 x 55 mm switch insert, ( ) Surface-mounted ( ) Flush-mounted |
|  | ......... pcs. .................. € .................. € GEZE E 70 room temperature regulator for automatic control of the room temperature Adjustment of room temperature from 5 °C to 30 °C and switchover manual-automatic operation, (1 piece) |
|  | ......... pcs. .................. € .................. € GEZE GC 240 RS rain sensor for the automatic closing of windows in case of rain in ventilation mode, rain sensor (heated electrically) with integrated control panel (1 piece) |
|  | ......... pcs. .................. € .................. € GEZE rain/wind control for the automatic closing of windows in case of rain/wind in ventilation mode, consisting of weather station with rain and wind sensor (heated electrically), control panel (1 piece) |
|  | REMARK Electrical cable routing and connection on site by an electrical contractor according to the GEZE cable diagrams. The type of cable to be used is to be determined with the respective local authorities. |
|  | ......... pcs. .................. € .................. € GEZE weather sensor system comprising ( ) GC 401 RS rain sensor ( ) GC 402 WVS wind sensor ( ) GC 403 WDS wind direction sensor (rain and wind sensor needed) For the automatic rain/wind control of ventilation operation and / or activation of SHEV depending on the wind direction (setting via the MBZ 300 software) |
| 1.20 | ......... pcs. .................. € .................. € Installation and functional test Installation and functional test by an expert authorised by the manufacturer. |
| 1.21 | ......... pcs. .................. € .................. € Start-up and official approval Official approval of the complete smoke and heat extraction system by an officially recognised expert, who also hands over the acceptance certificates. |
| 1.22 | ......... pcs. .................. € .................. € Maintenance and testing of smoke and heat extraction systems (optional position) Service package for maintenance and testing according to ASR A1.6, DIN 18232 as well as according to manufacturer’s specification with the following performance features: - One maintenance per contract year - Free provision and updating of the test documents - Attachment of the inspection sticker - Fault diagnosis and repair jobs during the contract period will be carried out at reduced hourly rates - Service technicians will be deployed within 24 hours of the message being received from Monday – Friday between 7 am and 5 pm without surcharges - Personal availability at the help desk 24 hours a day, 365 days a year - Contract run time: 2 years |
| 1.23 | Service maintenance - comfort package Service maintenance (optional position) Comfort service package for maintenance and accident prevention inspection in accordance with ASR A1.6, DIN 18232 as well as according to manufacturer’s specification with the following performance features: - Extension of the warranty to 36 months (condition: the maintenance contract is concluded 3 months after the commissioning date at the latest) - One maintenance per contract year - Free provision and updating of the test documents - Attachment of the inspection sticker - No separate charging for services and travel costs during the warranty period - No separate charging for consumables up to € 25 per maintenance - No separate charging for working hours when spare parts are replaced during the maintenance - Personal availability at the help desk 24 hours a day, 365 days a year - Contract run time: 3 years |
| 1.24 | ......... pcs. .................. € .................. € Delivery and installation Wiring to be carried out on site by an electrical contractor according to the GEZE cable plan. Delivery, installation and commissioning through plant fitters or service partner. Safety analysis, instruction of the operator as to how the system works and handing over of the documentation. Annual maintenance and technical inspection by an expert authorised by the manufacturer incl. documentation of the inspection in an inspection log. |